## Cover
Cable Sizing & Voltage Drop (IEC)
Conductor sizing for current, voltage drop and adiabatic withstand (IEC-style) — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Conductor sizing for current, voltage drop and adiabatic withstand (IEC-style)
EngiMetric · https://engimetric.com

## Summary
Cable Sizing & Voltage Drop (IEC)
Master verdict | PASS
Key inputs
Load | 45 | kW
Power factor | 0.9 | —
Line-line voltage | 0.4 | kV
Cable length (one way) | 60 | m
Prospective fault current | 6 | kA
Fault clearance time | 0.1 | s
Adiabatic k factor | 115 | —
Key outputs
Design current Ib | 72.1688 | A
Voltage drop | 0.002625 | %
Min adiabatic size | 16.4988 | mm²
Checks at a glance
Voltage drop within limit | PASS
Selected size ≥ adiabatic minimum | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Load | 45 | kW | load schedule
Power factor | 0.9 | — | load data
Line-line voltage | 0.4 | kV | system voltage
Cable length (one way) | 60 | m | routing
Conductor mV/A/m (selected size) | 1.4 | mV/A/m | cable tables (user)
Voltage drop limit | 4 | % | design criterion
Selected conductor cross-section | 25 | mm² | cable tables (user)
Prospective fault current | 6 | kA | discrimination study
Fault clearance time | 0.1 | s | protective device
Adiabatic k factor | 115 | — | material/temperature (tables, user)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Design current | 72.1688 | A | [1] — 3-phase balanced
Voltage drop | 0.0105 | V | [1] — mV→V
Voltage drop | 0.002625 | % | [1]
Minimum adiabatic size | 16.4988 | mm² | [1] — S ≥ √(I²t)/k

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Design current Ib | 72.1688 | A | [1]
Voltage drop | 0.002625 | % | [1]
Min adiabatic size | 16.4988 | mm² | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Voltage drop within limit | ≤ entered limit | PASS | [1]
Selected size ≥ adiabatic minimum | S ≥ √(I²t)/k | PASS | [1]
Power factor within range | 0.5–1 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | IEC 60364-5-52 / BS 7671 method; cable and k tables are user-supplied
Equations used
Design current | Ib = P/(√3·V·pf)
Voltage drop | ΔV% = √3·(mV/A/m)·Ib·L·100/(V·1000)
Adiabatic | S ≥ √(I²t)/k

## Notes & Assumptions
Notes & Assumptions
1. mV/A/m, k and the ampacity tables are governance inputs from your cable schedule — never embedded here.
2. Ampacity/dereating factors are separate checks not included in this screening.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.