## Cover
Compressed Air Demand & Receiver
Peak FAD demand and receiver volume estimate — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Peak FAD demand and receiver volume estimate
EngiMetric · https://engimetric.com

## Summary
Compressed Air Demand & Receiver
Master verdict | PASS
Key inputs
Peak tool demand | 300 | L/s
Compressor output (FAD) | 240 | L/s
Storage time required | 3 | min
Upper pressure (absolute) | 8 | bar(a)
Lower pressure (absolute) | 6.5 | bar(a)
Key outputs
Peak deficit | 60 | L/s
Receiver volume | 7.2936 | m³
Checks at a glance
Deficit positive (else no receiver needed) | PASS
Pressure band positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Peak tool demand | 300 | L/s | tooling audit
Compressor output (FAD) | 240 | L/s | machine rating (ISO 1217)
Storage time required | 3 | min | operating strategy
Upper pressure (absolute) | 8 | bar(a) | system setpoint
Lower pressure (absolute) | 6.5 | bar(a) | system setpoint

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Deficit vs compressor | 60 | L/s | [1]
Receiver volume | 7.2936 | m³ | [1] — isentropic-free simple storage

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Peak deficit | 60 | L/s | [1]
Receiver volume | 7.2936 | m³ | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Deficit positive (else no receiver needed) | > 0 | PASS | [1]
Pressure band positive | P1 > P2 | PASS | [1]
Demand positive | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | ISO 1217 (reference conditions); plant receiver sizing practice
Equations used
Receiver volume | V = (Qdem − Qsup)·t·p_atm/(P1 − P2)

## Notes & Assumptions
Notes & Assumptions
1. Simple isothermal storage estimate; thermodynamic FAD conversions and pressure-drop allowance apply at design.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.