## Cover
Duct Sizing (Velocity / Friction)
Round/ rectangular duct sizing from flow and velocity or friction — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Round/ rectangular duct sizing from flow and velocity or friction
EngiMetric · https://engimetric.com

## Summary
Duct Sizing (Velocity / Friction)
Master verdict | PASS
Key inputs
Air flow | 3000 | m³/h
Design velocity | 6 | m/s
Duct length | 20 | m
Darcy friction factor | 0.02 | —
Rectangular side length b | 600 | mm
Key outputs
Round diameter | 420.5221 | mm
Rectangular side a | 231.4815 | mm
Friction pressure drop | 20.5459 | Pa
Checks at a glance
Flow positive | PASS
Velocity positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Air flow | 3000 | m³/h | zone supply
Design velocity | 6 | m/s | noise/sizing criterion (user)
Duct length | 20 | m | routing
Darcy friction factor | 0.02 | — | duct roughness/Re (user)
Rectangular side length b | 600 | mm | space constraint
Sizing method | velocity | — | velocity ¦ friction

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Flow in m³/s | 0.83333 | m³/s | [1]
Required area | 0.13889 | m² | [1]
Round diameter | 420.5221 | mm | [1]
Other rectangular side a | 231.4815 | mm | [1] — a = A/b
Diameter in m | 0.42052 | m | [1]
Friction pressure drop | 20.5459 | Pa | [1] — ρ = 1.2 kg/m³

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Round diameter | 420.5221 | mm | [1]
Rectangular side a | 231.4815 | mm | [1]
Friction pressure drop | 20.5459 | Pa | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Flow positive | > 0 | PASS | [1]
Velocity positive | > 0 | PASS | [1]
Method recognised | velocity ¦ friction | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | ASHRAE Fundamentals duct design equations (method-level)
Equations used
Area | A = Q/V; d = √(4A/π)
Friction | ΔP = f·(L/d)·ρ·V²/2

## Notes & Assumptions
Notes & Assumptions
1. The friction case uses your entered friction factor; fittings/junctions are extra static losses.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.