## Cover
Generator / Standby Power Sizing
Generator sizing from running and starting kVA — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Generator sizing from running and starting kVA
EngiMetric · https://engimetric.com

## Summary
Generator / Standby Power Sizing
Master verdict | PASS
Key inputs
Diversified running load | 200 | kVA
Largest motor — running kVA | 25 | kVA
Largest motor — starting kVA | 100 | kVA
Sizing margin | 10 | %
Key outputs
Running requirement | 220 | kVA
Starting requirement | 302.5 | kVA
Governing requirement | 302.5 | kVA
Checks at a glance
Running load positive | PASS
Starting kVA ≥ running kVA | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Diversified running load | 200 | kVA | load schedule
Largest motor — running kVA | 25 | kVA | motor data
Largest motor — starting kVA | 100 | kVA | LRC data (user)
Sizing margin | 10 | % | design policy

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Running requirement | 220 | kVA | [1]
Starting requirement | 302.5 | kVA | [1]
Governing requirement | 302.5 | kVA | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Running requirement | 220 | kVA | [1]
Starting requirement | 302.5 | kVA | [1]
Governing requirement | 302.5 | kVA | [1]
Headroom vs running | 10 | % | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Running load positive | > 0 | PASS | [1]
Starting kVA ≥ running kVA | motorStart ≥ motorRun | PASS | [1]
Starting governs check | informative | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Genset sizing practice / NFPA 110 form (starting kVA from motor LRC data)
Equations used
Requirements | governing = max(running, starting)·(1+margin)

## Notes & Assumptions
Notes & Assumptions
1. Starting kVA is machine-published (LRC); add voltage-drop-on-start checks against your transient tolerance.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.