## Cover
Heat Exchanger LMTD / Sizing
LMTD single-pass sizing for required area — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
LMTD single-pass sizing for required area
EngiMetric · https://engimetric.com

## Summary
Heat Exchanger LMTD / Sizing
Master verdict | PASS
Key inputs
Hot-side flow | 20 | kg/s
Hot inlet temperature | 90 | °C
Hot outlet temperature | 70 | °C
Cold inlet temperature | 15 | °C
Cold outlet temperature | 55 | °C
Overall heat transfer coefficient | 800 | W/m²K
LMTD correction factor | 0.95 | —
Key outputs
Duty | 1674.4 | kW
LMTD | 44.2492 | K
Required area | 49.7897 | m²
Checks at a glance
Temperature profile consistent | PASS
ΔT ends positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Hot-side flow | 20 | kg/s | process
Hot inlet temperature | 90 | °C | process
Hot outlet temperature | 70 | °C | process
Cold inlet temperature | 15 | °C | process
Cold outlet temperature | 55 | °C | process
Hot fluid specific heat | 4.186 | kJ/kgK | fluid (water)
Overall heat transfer coefficient | 800 | W/m²K | service correlation
LMTD correction factor | 0.95 | — | configuration charts (user)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Duty from hot side | 1674.4 | kW | [1] — kW since cp in kJ/kgK
Hot end ΔT | 35 | K | [1]
Cold end ΔT | 55 | K | [1]
Log mean temperature difference | 44.2492 | K | [1]
Required heat transfer area | 49.7897 | m² | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Duty | 1674.4 | kW | [1]
LMTD | 44.2492 | K | [1]
Required area | 49.7897 | m² | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Temperature profile consistent | Th1 > Th2, Tc2 > Tc1 | PASS | [1]
ΔT ends positive | > 0 | PASS | [1]
U-value positive | > 0 | PASS | [1]
Correction factor within range | 0.5–1 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Kern; Incropera heat-exchanger fundamentals (LMTD method)
Equations used
Duty and LMTD | Q = ṁ·cp·ΔT; ΔTlm = (ΔT1 − ΔT2)/ln(ΔT1/ΔT2)
Area | A = Q / (U·F·ΔTlm)

## Notes & Assumptions
Notes & Assumptions
1. Counter-current single pass; F from charts assumes your configuration (user-supplied).
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.