## Cover
HVAC Cooling / Heating Load (Simplified)
Simplified sensible cooling/ heating load by component (CLTD-style) — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Simplified sensible cooling/ heating load by component (CLTD-style)
EngiMetric · https://engimetric.com

## Summary
HVAC Cooling / Heating Load (Simplified)
Master verdict | PASS
Key inputs
Wall area | 70 | m²
Wall U-value | 0.5 | W/m²K
Glazing area | 20 | m²
Glazing U-value | 2.6 | W/m²K
Design temperature difference | 25 | K
Infiltration air changes | 1.5 | 1/h
Internal gains | 900 | W
Key outputs
Total sensible load | 9618 | W
Total sensible load | 9.618 | kW
Checks at a glance
U-values positive | PASS
Temperature difference positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Wall area | 70 | m² | envelope
Wall U-value | 0.5 | W/m²K | construction assembly (user)
Roof area | 60 | m² | envelope
Roof U-value | 0.35 | W/m²K | construction assembly (user)
Glazing area | 20 | m² | envelope
Glazing U-value | 2.6 | W/m²K | fenestration (user)
Design temperature difference | 25 | K | design conditions
Solar cooling load (SCL) | 150 | W/m² | CLTD tables (user)
Infiltration air changes | 1.5 | 1/h | tightness assumption (user)
Room volume | 240 | m³ | space
Internal gains | 900 | W | occupants/equipment

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Wall conduction | 875 | W | [1]
Roof conduction | 525 | W | [1]
Glazing conduction | 1300 | W | [1]
Solar load through glazing | 3000 | W | [1]
Infiltration load | 3018 | W | [1] — ρ·cp at ~20 °C
Total sensible load | 9618 | W | [1]
Total sensible load | 9.618 | kW | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Conduction subtotal | 875 | W | [1]
Total sensible load | 9618 | W | [1]
Total sensible load | 9.618 | kW | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
U-values positive | > 0 | PASS | [1]
Temperature difference positive | > 0 | PASS | [1]
Infiltration sensible | 0–6 ACH | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | ASHRAE Handbook—Fundamentals method structure; coefficients are user-supplied
Equations used
Conduction | Q = U·A·ΔT
Infiltration | Q = ACH·V·ρ·cp·ΔT/3600
Solar (simplified) | Q = SCL·A_glass

## Notes & Assumptions
Notes & Assumptions
1. Screening tool only — NOT a full RTS/heat-balance calculation; latent load and coil sizing are separate.
2. U-values, SCL and ACH are governing inputs from your design data — never defaults from code.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.