## Cover
Lighting Design (Lumen Method)
Luminaire count and spacing by the lumen method — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Luminaire count and spacing by the lumen method
EngiMetric · https://engimetric.com

## Summary
Lighting Design (Lumen Method)
Master verdict | PASS
Key inputs
Room area | 120 | m²
Target illuminance | 300 | lux
Lumens per luminaire | 13500 | lm
Utilisation factor | 0.7 | —
Light loss factor | 0.8 | —
Key outputs
Luminaire count | 5 | nos
Installed illuminance | 315 | lux
Approx. grid spacing | 4.899 | m
Checks at a glance
Lumens per luminaire positive | PASS
Utilisation factor within range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Room area | 120 | m² | space
Target illuminance | 300 | lux | task level (user)
Lumens per luminaire | 13500 | lm | luminaire data
Utilisation factor | 0.7 | — | layout/reflectances (user)
Light loss factor | 0.8 | — | maintenance/surface-LDD (user)
Room length | 12 | m | space
Room width | 10 | m | space

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Luminaire count | 5 | nos | [1] — N = E·A/(F·UF·LLF)
Installed illuminance | 315 | lux | [1]
Area per luminaire | 24 | m² | [1]
Equivalent spacing (square grid) | 4.899 | m | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Luminaire count | 5 | nos | [1]
Installed illuminance | 315 | lux | [1]
Approx. grid spacing | 4.899 | m | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Lumens per luminaire positive | > 0 | PASS | [1]
Utilisation factor within range | 0.2–1 | PASS | [1]
Light loss factor within range | 0.5–1 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Lumen method (CIBSE/IES lighting guides, universal)
Equations used
Lumen method | N = E·A/(F·UF·LLF)

## Notes & Assumptions
Notes & Assumptions
1. Spacing is a square-grid approximation; lumens, UF and LLF come from photometric data — enter them.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.