## Cover
Pipe Head Loss (Hazenâ€“Williams / Darcyâ€“Weisbach)
Friction head loss by Hazen–Williams and Darcy–Weisbach (Swamee–Jain friction) — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Friction head loss by Hazen–Williams and Darcy–Weisbach (Swamee–Jain friction)
EngiMetric · https://engimetric.com

## Summary
Pipe Head Loss (Hazenâ€“Williams / Darcyâ€“Weisbach)
Master verdict | WARN
Key inputs
Flow Q | 40 | m³/h
Pipe internal diameter | 80 | mm
Pipe length | 300 | m
Key outputs
Friction loss (H-W) | 23.8658 | m
Friction loss (D-W) | 19.0629 | m
Checks at a glance
Methods agree within 20% | WARN
Velocity within recommended range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Flow Q | 40 | m³/h | duty
Pipe length | 300 | m | routing
Pipe internal diameter | 80 | mm | pipe spec
Hazen–Williams coefficient C | 120 | — | pipe material (published ranges)
Absolute roughness | 0.05 | mm | pipe material (published ranges)
Water temperature | 20 | °C | measured / design

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Flow in m³/s | 0.011111 | m³/s | [1]
Diameter in m | 0.08 | m | [1]
Flow velocity | 2.2105 | m/s | [1]
Kinematic viscosity | 1.4e-06 | m²/s | [1] — water ν fit (m²/s)
Reynolds number | 126313.4732 | — | [1]
Darcy friction factor (Swamee–Jain) | 0.020405 | — | [1]
Friction loss (Hazen–Williams) | 23.8658 | m | [1]
Friction loss (Darcy–Weisbach) | 19.0629 | m | [1]
Agreement between methods | 25.1951 | % | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Velocity | 2.2105 | m/s | [1]
Reynolds number | 126313.4732 | — | [1]
Friction loss (H-W) | 23.8658 | m | [1]
Friction loss (D-W) | 19.0629 | m | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Methods agree within 20% | ≤ 20% | WARN | [1]
Velocity within recommended range | 0.5–2.5 m/s | PASS | [1]
Distance to next | — | PASS | [1]
Master verdict
Overall result | PASS when every check passes | WARN

## Reference
References
[1] | Hazen–Williams; Darcy–Weisbach; Swamee & Jain (1976) approximation (standard hydraulics texts)
Equations used
Hazen–Williams friction | hf = 10.67·L·Q^1.852 / (C^1.852·D^4.8704)
Darcy–Weisbach with Swamee–Jain | hf = f·L/D·v²/(2g); f = 0.25/(log10(k/3.7D + 5.74/Re^0.9))^2

## Notes & Assumptions
Notes & Assumptions
1. Two independent methods are shown and cross-checked — divergence flags input or applicability issues.
2. Kinematic viscosity uses a simple water fit; use measured values when precision matters.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.