## Cover
Pipe Sizing by Velocity & Pressure
Pipe sizing from velocity and friction (Hazen–Williams) with selected DN check — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Pipe sizing from velocity and friction (Hazen–Williams) with selected DN check
EngiMetric · https://engimetric.com

## Summary
Pipe Sizing by Velocity & Pressure
Master verdict | PASS
Key inputs
Design flow Q | 60 | m³/h
Selected internal diameter | 150 | mm
Maximum design velocity | 2.5 | m/s
Key outputs
Min diameter (velocity) | 92.1318 | mm
Min diameter (friction) | 142.8808 | mm
Velocity at selected size | 0.94314 | m/s
Checks at a glance
Selected size ≥ velocity minimum | PASS
Selected size ≥ friction minimum | PASS
Velocity at selected size within band | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Design flow Q | 60 | m³/h | design duty
Maximum design velocity | 2.5 | m/s | system criterion
Pipe length | 400 | m | routing
Hazen–Williams coefficient C | 120 | — | pipe material (published ranges)
Allowable friction loss | 4 | m | pressure budget
Selected internal diameter | 150 | mm | chosen DN (internal)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Flow in m³/s | 0.016667 | m³/s | [1]
Min diameter for velocity | 92.1318 | mm | [1]
Min diameter for friction budget | 142.8808 | mm | [1]
Selected diameter in m | 0.15 | m | [1]
Velocity at selected size | 0.94314 | m/s | [1]
Friction at selected size | 3.1565 | m | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Min diameter (velocity) | 92.1318 | mm | [1]
Min diameter (friction) | 142.8808 | mm | [1]
Velocity at selected size | 0.94314 | m/s | [1]
Friction at selected size | 3.1565 | m | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Velocity at selected size within band | 0.5–2.5 m/s (informative) | PASS | [1]
Selected size ≥ velocity minimum | dSel ≥ dminVel | PASS | [1]
Selected size ≥ friction minimum | dSel ≥ dminLoss | PASS | [1]
Length positive | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Hazen–Williams; EngiMetric hydraulics engines (calculatePipeSizing velocity band)
Equations used
Diameter from max velocity | d ≥ √(4Q/(π·vmax))
Diameter from friction budget | d = (10.67·L·Q^1.852 / (C^1.852·hf))^(1/4.8704)

## Notes & Assumptions
Notes & Assumptions
1. Velocity band is an informative EngiMetric engine constant, not a code limit.
2. Standard nominal sizes (DN) come from your pipe catalogue — the workbook compares against internal diameter you enter.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.