## Cover
Pump Sizing & Duty Point
Pump hydraulic power and motor input at the duty point — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Pump hydraulic power and motor input at the duty point
EngiMetric · https://engimetric.com

## Summary
Pump Sizing & Duty Point
Master verdict | PASS
Key inputs
Flow | 100 | m³/h
Total dynamic head | 40 | m
Pump efficiency | 70 | %
Motor efficiency | 93 | %
Key outputs
Hydraulic power | 10.9 | kW
Shaft power | 15.5714 | kW
Motor input power | 16.7435 | kW
Checks at a glance
Flow and head positive | PASS
Efficiency within range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Flow | 100 | m³/h | duty
Total dynamic head | 40 | m | system curve
Pump efficiency | 70 | % | manufacturer curve
Motor efficiency | 93 | % | motor data
Fluid density | 1000 | kg/m³ | fluid (water)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Flow in m³/s | 0.027778 | m³/s | [1]
Hydraulic power | 10.9 | kW | [1]
Shaft power | 15.5714 | kW | [1]
Motor input power | 16.7435 | kW | [1]
Specific energy | 0.15571 | kWh/m³ | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Hydraulic power | 10.9 | kW | [1]
Shaft power | 15.5714 | kW | [1]
Motor input power | 16.7435 | kW | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Efficiency within range | 20–95 % | PASS | [1]
Flow and head positive | > 0 | PASS | [1]
Motor efficiency within range | 70–99 % | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Pump power equation (universal fluid mechanics); EngiMetric hydraulics engine
Equations used
Hydraulic power | P = ρ·g·Q·H
Shaft & motor | Ps = P/η; Pm = Ps/η_m

## Notes & Assumptions
Notes & Assumptions
1. Duty point should come from the system curve intersection with the manufacturer curve — enter that H.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.