## Cover
Pump Total Dynamic Head
Total dynamic head by Hazen–Williams friction plus minor and residual terms — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Total dynamic head by Hazen–Williams friction plus minor and residual terms
EngiMetric · https://engimetric.com

## Summary
Pump Total Dynamic Head
Master verdict | PASS
Key inputs
Flow Q | 60 | m³/h
Pipe internal diameter | 100 | mm
Static head (delivery − suction) | 20 | m
Key outputs
Total dynamic head | 55.4285 | m
Velocity | 2.1221 | m/s
Checks at a glance
Velocity within recommended range | PASS
TDH positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Flow Q | 60 | m³/h | duty
Pipe length | 500 | m | routing
Pipe internal diameter | 100 | mm | pipe spec
Hazen–Williams coefficient C | 120 | — | pipe material (published ranges)
Static head (delivery − suction) | 20 | m | layout levels
Minor losses (fittings/system) | 2 | m | fitting count × loss values
Required residual pressure head | 5 | m | system requirement

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Flow in m³/s | 0.016667 | m³/s | [1]
Diameter in m | 0.1 | m | [1]
Flow velocity | 2.1221 | m/s | [1]
Friction head loss | 28.4285 | m | [1] — Hazen–Williams
Total dynamic head TDH | 55.4285 | m | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Friction loss | 28.4285 | m | [1]
Velocity | 2.1221 | m/s | [1]
Total dynamic head | 55.4285 | m | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Velocity within recommended range | 0.5–2.5 m/s | PASS | [1]
C coefficient plausible | > 40 | PASS | [1]
TDH positive | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Hazen–Williams equation (standard hydraulics); EngiMetric hydraulics engine velocity constants
Equations used
Hazen–Williams friction | hf = 10.67 · L · Q^1.852 / (C^1.852 · D^4.8704), Q in m³/s, D in m
Total dynamic head | TDH = static ± friction ± minor + residual

## Notes & Assumptions
Notes & Assumptions
1. Hazen–Williams applies to water in turbulent flow; deviations increase for oils/glycols.
2. Recommended velocity band (0.5–2.5 m/s) is the engine constant — an informative band, not a code limit.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.