## Cover
RO Membrane Element Count
Membrane element count from flow, flux and element area — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Membrane element count from flow, flux and element area
EngiMetric · https://engimetric.com

## Summary
RO Membrane Element Count
Master verdict | PASS
Key inputs
Permeate/design flow | 80 | m³/h
Design flux | 20 | L/m²·h
Key outputs
Elements required | 108 | no.
Flux at selected count | 19.9124 | L/m²·h
Checks at a glance
Flux within typical range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Permeate/design flow | 80 | m³/h | design duty
Design flux | 20 | L/m²·h | design value within typical 10–40
Membrane area per element | 37.2 | m² | element datasheet (e.g., 8 inch spiral)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Required elements (continuous) | 107.5269 | — | [1]
Required elements (whole) | 108 | no. | [1] — round up
Actual flux at whole count | 19.9124 | L/m²·h | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Elements required | 108 | no. | [1]
Flux at selected count | 19.9124 | L/m²·h | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Flux within typical range | 10–40 L/m²·h | PASS | [1]
Design flow positive | > 0 | PASS | [1]
Element area positive | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | EngiMetric RO element-count engine (typical flux range 10–40 L/m²·h)
Equations used
Element count from flux | elements = Q · 1000 / (flux · area)

## Notes & Assumptions
Notes & Assumptions
1. Pre-design screen only: array staging, pressure-vessel loading and element type selection require vendor design software.
2. Typical flux band is the engine constant; the governing value is the user-design flux.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.