## Cover
RO Energy & Operating Cost
RO pump energy, specific energy and operating unit cost — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
RO pump energy, specific energy and operating unit cost
EngiMetric · https://engimetric.com

## Summary
RO Energy & Operating Cost
Master verdict | PASS
Key inputs
Permeate flow Qp | 75 | m³/h
Feed pressure p | 60 | bar
Combined pump/motor efficiency η | 75 | %
Key outputs
Motor power | 163.4442 | kW
Specific energy SEC | 2.1793 | kWh/m³
OPEX per m³ | 0.26613 | $/m³
Checks at a glance
Efficiency within physical range | PASS
Permeate flow positive | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Permeate flow Qp | 75 | m³/h | RO performance data
Feed pressure p | 60 | bar | operating data
Combined pump/motor efficiency η | 75 | % | manufacturer / system data
Electricity tariff | 0.09 | $/kWh | utility tariff
Annual operating hours | 8000 | h/yr | operation plan
Chemical cost | 0.04 | $/m³ | consumables budget
Membrane replacement cost | 0.03 | $/m³ | lifecycle estimate

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Hydraulic power Phyd | 122.5831 | kW | [1] — Phyd = ρgHQ; 1 bar ≈ 10.2 m
Motor power (shaft) | 163.4442 | kW | [1]
Specific energy SEC | 2.1793 | kWh/m³ | [1]
Annual energy use | 1307553.3333 | kWh/yr | [1]
Annual energy cost | 117679.8 | $/yr | [1]
Annual permeate volume | 600000 | m³/yr | [1]
Annual chemical cost | 24000 | $/yr | [1]
Annual membrane cost | 18000 | $/yr | [1]
Total OPEX per m³ | 0.26613 | $/m³ | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Hydraulic power | 122.5831 | kW | [1]
Motor power | 163.4442 | kW | [1]
Specific energy SEC | 2.1793 | kWh/m³ | [1]
OPEX per m³ | 0.26613 | $/m³ | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Efficiency within physical range | 0 < η ≤ 100% | PASS | [1]
Permeate flow positive | > 0 | PASS | [1]
Pressure positive | > 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | EngiMetric RO energy & opex engines (calculateRoEnergy, calculateRoOpex)
Equations used
Hydraulic power at operating pressure | Phyd = ρ·g·Q·H (1 bar ≈ 10 m head)
Specific energy and operating unit cost | SEC = P_motor/Qp; OPEX = (energy + chemicals + membranes)/volume

## Notes & Assumptions
Notes & Assumptions
1. Single-stage duty-point estimate; ignores energy-recovery devices and part-load effects.
2. Energy-recovery devices can cut SEC materially at high recovery — enter actual operating data when available.
3. All costs are user-entered; no default prices are invented.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.