## Cover
RO Scaling & Saturation Indices
Langelier (LSI) and Ryznar (RSI) saturation indices for concentrate — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Langelier (LSI) and Ryznar (RSI) saturation indices for concentrate
EngiMetric · https://engimetric.com

## Summary
RO Scaling & Saturation Indices
Master verdict | PASS
Key inputs
Concentrate TDS | 49000 | mg/L
Temperature | 25 | °C
pH | 7.8 | —
Key outputs
Langelier index | 0.71088 | —
Ryznar index | 6.3782 | —
Checks at a glance
LSI in stable band (indicative) | PASS
RSI in stable band (indicative) | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Concentrate TDS | 49000 | mg/L | concentrate analysis
Temperature | 25 | °C | measured
Calcium as CaCO₃ | 900 | mg/L | concentrate analysis
Alkalinity as CaCO₃ | 130 | mg/L | concentrate analysis
pH | 7.8 | — | measured

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
A (temperature/TDS constant) | 0.36902 | — | [1] — A = (log TDS − 1)/10
B (temperature constant) | 2.0883 | — | [1]
C (calcium term) | 2.5542 | — | [1]
D (alkalinity term) | 2.1139 | — | [1]
Saturation pH (pHs) | 7.0891 | — | [1] — Langelier saturation pH
Langelier index LSI | 0.71088 | — | [1]
Ryznar index RSI | 6.3782 | — | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Langelier index | 0.71088 | — | [1]
Ryznar index | 6.3782 | — | [1]
Saturation pH | 7.0891 | — | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
LSI in stable band (indicative) | −1 ≤ LSI ≤ 1 | PASS | [1]
RSI in stable band (indicative) | 5.5–7.0 | PASS | [1]
TDS positive | > 0 | PASS | [1]
Temperature in range | 0–50 °C | PASS | [1]
pH in range | 0–14 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Langelier (1936); Ryznar (1944) — standard saturation-index method (public)
Equations used
Langelier saturation pH | pHs = (9.3 + A + B) − (C + D); A=(log TDS −1)/10; B=−13.12 log(T+273)+34.55; C=log Ca −0.4; D=log Alk
Indices | LSI = pH − pHs; RSI = 2·pHs − pH

## Notes & Assumptions
Notes & Assumptions
1. Indices are indicative tendency tools, not scaling-rate predictors.
2. LSI/RSI classic constants apply up to moderate TDS. For high-TDS concentrate (TDS > 10 000 mg/L) use the Stiff & Davis S&DSI — available in the EngiMetric RO Scaling Calculator.
3. A WARN here flags the interpretation band, not an input error.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.