## Cover
UPS & Battery Sizing
UPS kVA and battery ampere-hour sizing for autonomy — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
UPS kVA and battery ampere-hour sizing for autonomy
EngiMetric · https://engimetric.com

## Summary
UPS & Battery Sizing
Master verdict | PASS
Key inputs
Load | 40 | kW
Load power factor | 0.9 | —
Autonomy | 0.5 | h
DC bus voltage | 480 | V
Inverter/battery efficiency | 0.9 | —
Depth of discharge limit | 80 | %
Key outputs
UPS rating | 44.4444 | kVA
Battery capacity | 57.8704 | Ah
Cells (2 V nominal) | 240 | nos
Checks at a glance
Load positive | PASS
DoD within range | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Load | 40 | kW | critical load
Load power factor | 0.9 | — | load data
Autonomy | 0.5 | h | requirement
DC bus voltage | 480 | V | system architecture
Inverter/battery efficiency | 0.9 | — | system data
Depth of discharge limit | 80 | % | battery type (user)

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
UPS rating | 44.4444 | kVA | [1]
Battery capacity | 57.8704 | Ah | [1] — Ah = P·t/(V·η·DoD)
Cells (2 V nominal) | 240 | nos | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
UPS rating | 44.4444 | kVA | [1]
Battery capacity | 57.8704 | Ah | [1]
Cells (2 V nominal) | 240 | nos | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Power factor within range | 0.5–1 | PASS | [1]
Load positive | > 0 | PASS | [1]
DoD within range | 10–100 % | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | IEEE Std 485 battery sizing method (form adopted for screening)
Equations used
UPS rating | kVA = kW/pf
Battery | Ah = P·t/(V·η·DoD)

## Notes & Assumptions
Notes & Assumptions
1. IEEE 485 adds temperature/aging correction factors — apply them as factors around this raw estimate.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.