## Cover
Water Hammer (Joukowsky Surge)
Joukowsky surge pressure from instantaneous velocity change — [1]
Version 0.1 · Generated 2026-09-24
Read first
This is a guided engineering calculation workbook, not a stamped design document.
Fill only yellow Input cells. Calculated and result cells are protected-by-convention (never hand-edit).
Review the Checks sheet — address any WARN or FAIL before use.
Enter governing code/table values (e.g. ampacity tables, demand factors, U-values) from your governing standard where a Source column asks for it.
Verify all results against project data and applicable standards with a qualified engineer.
Workbook structure
Inputs — every user entry (yellow).
Calculations — transparent formulas with reference IDs.
Outputs — final results (blue).
Checks — PASS/WARN/FAIL verification vs the reference limits.
Reference — sources cited by ID ([1], …).
Notes & Assumptions — declared limitations and assumptions.
Method
Joukowsky surge pressure from instantaneous velocity change
EngiMetric · https://engimetric.com

## Summary
Water Hammer (Joukowsky Surge)
Master verdict | PASS
Key inputs
Pipe internal diameter | 100 | mm
Pipe wall thickness | 5.8 | mm
Pipe modulus of elasticity | 210000000000 | Pa
Velocity change (sudden closure) | 1.5 | m/s
Key outputs
Pressure-wave speed | 1365.0719 | m/s
Surge pressure rise | 20.4761 | bar
Checks at a glance
Wave speed plausible (water pipelines) | PASS
Velocity change non-negative | PASS
Version 0.1 · EngiMetric workbook library

## Inputs
Inputs — yellow cells: enter your values; source prompts governing choices
Fluid density | 1000 | kg/m³ | fluid (water: 1000)
Fluid bulk modulus | 2200000000 | Pa | fluid property (water: 2.2e9)
Pipe internal diameter | 100 | mm | pipe spec
Pipe wall thickness | 5.8 | mm | pipe spec
Pipe modulus of elasticity | 210000000000 | Pa | pipe material (steel: 2.1e11)
Velocity change (sudden closure) | 1.5 | m/s | initial velocity at closure

## Calculations
Calculations — transparent formulas; [n] is the reference ID (see Reference sheet)
Diameter in m | 0.1 | m | [1]
Wall thickness in m | 0.0058 | m | [1]
Pressure-wave speed c | 1365.0719 | m/s | [1]
Surge pressure rise | 2047607.9195 | Pa | [1] — Joukowsky Δp = ρ·c·Δv
Surge pressure rise | 20.4761 | bar | [1]

## Outputs
Outputs — final results (formula-driven; never hard-typed)
Pressure-wave speed | 1365.0719 | m/s | [1]
Surge pressure rise | 20.4761 | bar | [1]

## Checks
Checks — each row must land PASS (WARN acceptable when documented)
Wave speed plausible (water pipelines) | 300–1500 m/s | PASS | [1]
Diameter positive | > 0 | PASS | [1]
Wall thickness positive | > 0 | PASS | [1]
Velocity change non-negative | ≥ 0 | PASS | [1]
Master verdict
Overall result | PASS when every check passes | PASS

## Reference
References
[1] | Joukowsky (1898); Chaudhry; Wylie & Streeter — hydraulic transients texts
Equations used
Wave speed | c = 1/√(ρ·(1/K + D/(e·E)))
Surge rise (Joukowsky) | Δp = ρ·c·Δv

## Notes & Assumptions
Notes & Assumptions
1. Instantaneous-closure worst case. Real closure times, surge tanks and air valves reduce the rise.
2. Manual estimation only for a single pipe; complex networks need transient analysis software.
Disclaimer
Governed by the EngiMetric Workbook Standard v1.0. Values computed depend entirely on the data entered.
Code/table-derived factors are user inputs prompted by their Source column — no copyrighted tables are embedded.
Not a substitute for qualified, licensed engineering review.